## Agglomeration 1
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: TARGU MURES
Agglomeration 2: LIVEZENI+POIENITA+IVANESTI+SANISOR+CORUNCA+BOZENI (group)
Agglomeration 3: ERNEI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 555724 | 555724
Size of agglomeration 2 | [PE] | 3890 | 3890
Size of agglomeration 3 | [PE] | 2935 | 2935
Size of agglomeration 4 | [PE] | 0 | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 562549
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 76412.05
Wastewater amount of agglomeration 2 | [m³/d] | 389
Wastewater amount of agglomeration 3 | [m³/d] | 293.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 77094.55
Connection details
Lenth of the transportation line | [m] | - | 25000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 77.364 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3 (according formula) | [€/PE] | - | 76.9704
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 17197207.4034 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 404000
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 308500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 17319856.5212
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 4262500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 17909707.4034 | 21618679.5212
Writting-off period | [years] | 40 | 40
| [€/a] | 447742.6851 | 540466.988
Cost of capital, average | [%] | 3 | 3
| [€/a] | 537291.2221 | 648560.3856
Annual costs civil works | [€/a] | 985033.9072 | 1189027.3737
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 25795811.105 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 598500
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 455250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 25979784.7819
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 26849561.105 | 25983484.7819
Writting-off period | [years] | 12 | 12
| [€/a] | 2237463.4254 | 2165290.3985
Cost of capital, average | [%] | 3 | 3
| [€/a] | 805486.8332 | 779504.5435
Annual costs mechanical and electrical equipment | [€/a] | 3042950.2586 | 2944794.9419
Annual costs I. (Investment) | [€/a] | 4027984.1658 | 4133822.3156
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 1073982.4442 | 1039339.3913
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 76412.05 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 72205.031 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 389 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.3202 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 513.5399 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 293.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.3783 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 404.5416 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 73123.1124
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 682.5
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 30.9969
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 77094.55
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 0.61645
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 47524.7652
Total A 1 - A 2 | [kWh/d] | 73123.1124 | 47555.7621
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 10968.4669 | 7133.3643
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 10968.4669 | 7133.3643
Annual costs IV. (consumption) | [€/a] | 4003490.4059 | 2603677.9757
Summary
Annual costs I. (Investment) | [€/a] | 4027984.1658 | 4133822.3156
Annual costs II. (Maintenance / Repairs) | [€/a] | 1073982.4442 | 1039339.3913
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 4003490.4059 | 2603677.9757
Total annual costs | [€/a] | 9193057.0158 | 7820639.6826
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 3
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SIGHISOARA
Agglomeration 2: AUREL VLAICU
Agglomeration 3: ALBESTI
Agglomeration 4: BOIU+TOPA
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 34552 | 34552
Size of agglomeration 2 | [PE] | 98 | 98
Size of agglomeration 3 | [PE] | 3370 | 3370
Size of agglomeration 4 | [PE] | 1883 | 1883
Size of agglomeration 1+ 2+3+4 | [PE] |  | 39903
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 4750.9
Wastewater amount of agglomeration 2 | [m³/d] | 9.8
Wastewater amount of agglomeration 3 | [m³/d] | 337
Wastewater amount of agglomeration 4 | [m³/d] | 188.3
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 5286
Connection details
Lenth of the transportation line | [m] | - | 13000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 400
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 246.926 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 232.5096
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 234.3
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 3412715.0048 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 24800
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 352000
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 203300
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 3711131.6443
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 3045900
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 3992815.0048 | 6793354.6443
Writting-off period | [years] | 40 | 40
| [€/a] | 99820.3751 | 169833.8661
Cost of capital, average | [%] | 3 | 3
| [€/a] | 119784.4501 | 203800.6393
Annual costs civil works | [€/a] | 219604.8253 | 373634.5054
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 5119072.5073 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 29700
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 520500
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 297450
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 5566697.4665
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 5966722.5073 | 5570397.4665
Writting-off period | [years] | 12 | 12
| [€/a] | 497226.8756 | 464199.7889
Cost of capital, average | [%] | 3 | 3
| [€/a] | 179001.6752 | 167111.924
Annual costs mechanical and electrical equipment | [€/a] | 676228.5508 | 631311.7129
Annual costs I. (Investment) | [€/a] | 895833.3761 | 1004946.2183
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 238668.9003 | 222815.8987
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 4750.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 4489.3297 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 9.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.3195 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 22.7308 | -
A 1.3 WWTP agglomeration 1
Wastewater amount of agglomeration 3 | [m³/d] | 337 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8895 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 636.7502 | -
A 1.4 WWTP agglomeration 2
Wastewater amount of agglomeration 4 | [m³/d] | 188.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5721 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 296.0279 | -
Total A 1 | [kWh/d] | 5444.8386
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 346.8
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 15.7505
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 5286
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 0.92434
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 4886.063
Total A 1 - A 2 | [kWh/d] | 5444.8386 | 4901.8135
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 816.7258 | 735.272
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 816.7258 | 735.272
Annual costs IV. (consumption) | [€/a] | 298104.9138 | 268374.2892
Summary
Annual costs I. (Investment) | [€/a] | 895833.3761 | 1004946.2183
Annual costs II. (Maintenance / Repairs) | [€/a] | 238668.9003 | 222815.8987
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 298104.9138 | 268374.2892
Total annual costs | [€/a] | 1564007.1901 | 1539936.4061
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 4
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: TARNAVENI+BOTORCA+BOBOHALMA (group)
Agglomeration 2: ADAMUS+CORNESTI+CRAIESTI+DAMBAU (group)
Agglomeration 3: GANESTI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 27323 | 27323
Size of agglomeration 2 | [PE] | 6135 | 6135
Size of agglomeration 3 | [PE] | 3875 | 3875
Size of agglomeration 4 | [PE] | 0 | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 37333
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 3756.9125
Wastewater amount of agglomeration 2 | [m³/d] | 613.5
Wastewater amount of agglomeration 3 | [m³/d] | 387.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1 + 2+3 | [m³/d] |  | 4757.9125
Connection details
Lenth of the transportation line | [m] | - | 13000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 400
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 272.3701 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 508.3842
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3 (according formula) | [€/PE] | - | 239.0675
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 234.3
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 2976786.9575 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 1247574.7348
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 402500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 3570042.7022
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 3045900
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 4626861.6922 | 6652265.7022
Writting-off period | [years] | 40 | 40
| [€/a] | 115671.5423 | 166306.6426
Cost of capital, average | [%] | 3 | 3
| [€/a] | 138805.8508 | 199567.9711
Annual costs civil works | [€/a] | 254477.3931 | 365874.6136
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 4465180.4362 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 1871362.1021
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 596250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 5355064.0534
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 6932792.5383 | 5358764.0534
Writting-off period | [years] | 12 | 12
| [€/a] | 577732.7115 | 446563.6711
Cost of capital, average | [%] | 3 | 3
| [€/a] | 207983.7762 | 160762.9216
Annual costs mechanical and electrical equipment | [€/a] | 785716.4877 | 607326.5927
Annual costs I. (Investment) | [€/a] | 1040193.8808 | 973201.2063
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 277311.7015 | 214350.5621
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 3756.9125 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.97952 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 3679.9714 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 613.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.2312 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 755.3461 | -
A 1.3 WWTP agglomeration 1
Wastewater amount of agglomeration 3 | [m³/d] | 387.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.3209 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 511.8623 | -
A 1.4 WWTP agglomeration 2
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 4947.1798
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 1001
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 45.4621
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 4757.9125
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 0.93381
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 4442.9854
Total A 1 - A 2 | [kWh/d] | 4947.1798 | 4488.4474
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 742.077 | 673.2671
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 742.077 | 673.2671
Annual costs IV. (consumption) | [€/a] | 270858.0945 | 245742.4977
Summary
Annual costs I. (Investment) | [€/a] | 1040193.8808 | 973201.2063
Annual costs II. (Maintenance / Repairs) | [€/a] | 277311.7015 | 214350.5621
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 270858.0945 | 245742.4977
Total annual costs | [€/a] | 1675963.6768 | 1477094.2662
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 5
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: LUDUS
Agglomeration 2: BOGATA
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 17650 | 17650
Size of agglomeration 2 | [PE] | 1609 | 1609
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2 | [PE] |  | 19259
No. of WTP modules | [items] | 1
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 2426.875
Wastewater amount of agglomeration 2 | [m³/d] | 160.9
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 2587.775
Connection details
Lenth of the transportation line | [m] | - | 1000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 326.9272 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2 (according formula) | [€/PE] | - | 315.2252
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 2308105.7351 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 175900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 2428369.0528
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 170500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 2484005.7351 | 2635192.0528
Writting-off period | [years] | 40 | 40
| [€/a] | 62100.1434 | 65879.8013
Cost of capital, average | [%] | 3 | 3
| [€/a] | 74520.1721 | 79055.7616
Annual costs civil works | [€/a] | 136620.3154 | 144935.5629
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 3462158.6027 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 256350
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 3642553.5792
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 3718508.6027 | 3646253.5792
Writting-off period | [years] | 12 | 12
| [€/a] | 309875.7169 | 303854.4649
Cost of capital, average | [%] | 3 | 3
| [€/a] | 111555.2581 | 109387.6074
Annual costs mechanical and electrical equipment | [€/a] | 421430.975 | 413242.0723
Annual costs I. (Investment) | [€/a] | 558051.2904 | 558177.6352
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 148740.3441 | 145850.1432
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 8760 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 43800 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 2426.875 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.0473 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 2541.6553 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 160.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5112 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 243.1522 | -
A 1.3 WWTP agglomeration 1
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 2
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 2784.8074
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 160.9
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 7.3075
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 2587.775
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.0334
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 2674.2065
Total A 1 - A 2 | [kWh/d] | 2784.8074 | 2681.5141
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 417.7211 | 402.2271
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 417.7211 | 402.2271
Annual costs IV. (consumption) | [€/a] | 152468.2078 | 146812.8942
Summary
Annual costs I. (Investment) | [€/a] | 558051.2904 | 558177.6352
Annual costs II. (Maintenance / Repairs) | [€/a] | 148740.3441 | 145850.1432
Annual costs III. (labour) | [€/a] | 43800 | 43800
Annual costs IV. (consumption) | [€/a] | 152468.2078 | 146812.8942
Total annual costs | [€/a] | 903059.8424 | 894640.6726
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 7
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: IERNUT
Agglomeration 2: SAFANTU GHEORGHE+CIPAU (group)
Agglomeration 3: LECHINTA
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 6704 | 6704
Size of agglomeration 2 | [PE] | 1509 | 1509
Size of agglomeration 3 | [PE] | 801 | 801
Size of agglomeration 4 | [PE] | 0 | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 9014
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 921.8
Wastewater amount of agglomeration 2 | [m³/d] | 150.9
Wastewater amount of agglomeration 3 | [m³/d] | 80.1
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 1152.8
Connection details
Lenth of the transportation line | [m] | - | 3500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 489.89 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3 (according formula) | [€/PE] | - | 432.8888
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 1313689.0749 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 165900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 95100
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 1560823.984
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 596750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 1574689.0749 | 2193896.984
Writting-off period | [years] | 40 | 40
| [€/a] | 39367.2269 | 54847.4246
Cost of capital, average | [%] | 3 | 3
| [€/a] | 47240.6722 | 65816.9095
Annual costs civil works | [€/a] | 86607.8991 | 120664.3341
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 1970533.6124 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 241350
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 135150
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 2341235.976
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 2347033.6124 | 2344935.976
Writting-off period | [years] | 12 | 12
| [€/a] | 195586.1344 | 195411.3313
Cost of capital, average | [%] | 3 | 3
| [€/a] | 70411.0084 | 70348.0793
Annual costs mechanical and electrical equipment | [€/a] | 265997.1427 | 265759.4106
Annual costs I. (Investment) | [€/a] | 352605.0419 | 386423.7447
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 93881.3445 | 93797.439
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 921.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 871.0484 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 150.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5261 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 230.2914 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 80.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6815 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 134.689 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 1236.0289
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 231
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 10.4913
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 1152.8
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.1608
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 1338.1412
Total A 1 - A 2 | [kWh/d] | 1236.0289 | 1348.6325
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 185.4043 | 202.2949
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 185.4043 | 202.2949
Annual costs IV. (consumption) | [€/a] | 67672.5826 | 73837.6268
Summary
Annual costs I. (Investment) | [€/a] | 352605.0419 | 386423.7447
Annual costs II. (Maintenance / Repairs) | [€/a] | 93881.3445 | 93797.439
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 67672.5826 | 73837.6268
Total annual costs | [€/a] | 601758.969 | 597858.8106
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 8
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BAND
Agglomeration 2: TRIPTELNIC
Agglomeration 3: VALEA RECE
Agglomeration 4: MARASESTI
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 3712 | 3712
Size of agglomeration 2 | [PE] | 137 | 137
Size of agglomeration 3 | [PE] | 297 | 297
Size of agglomeration 4 | [PE] | 323 | 323
Size of agglomeration 1+ 2+3+4 | [PE] |  | 4469
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 371.2
Wastewater amount of agglomeration 2 | [m³/d] | 13.7
Wastewater amount of agglomeration 3 | [m³/d] | 29.7
Wastewater amount of agglomeration 4 | [m³/d] | 32.3
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 446.9
Connection details
Lenth of the transportation line | [m] | - | 11000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 386200 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 28700
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 44700
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 47300
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 461900
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 1875500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 506900 | 2373723
Writting-off period | [years] | 40 | 40
| [€/a] | 12672.5 | 59343.075
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15207 | 71211.69
Annual costs civil works | [€/a] | 27879.5 | 130554.765
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 571800 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 35550
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 59550
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 63450
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 685350
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 730350 | 689050
Writting-off period | [years] | 12 | 12
| [€/a] | 60862.5 | 57420.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 21910.5 | 20671.5
Annual costs mechanical and electrical equipment | [€/a] | 82773 | 78092.3333
Annual costs I. (Investment) | [€/a] | 110652.5 | 208647.0983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 29214 | 27562
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 371.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 350.7628 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 13.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.2035 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 30.188 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 29.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9573 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 58.1331 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 32.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9324 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 62.4151 | -
Total A 1 | [kWh/d] | 501.499
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 43.4
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 1.9711
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 446.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2924
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 577.5758
Total A 1 - A 2 | [kWh/d] | 501.499 | 579.5469
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 75.2248 | 86.932
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 75.2248 | 86.932
Annual costs IV. (consumption) | [€/a] | 27457.0699 | 31730.1929
Summary
Annual costs I. (Investment) | [€/a] | 110652.5 | 208647.0983
Annual costs II. (Maintenance / Repairs) | [€/a] | 29214 | 27562
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 27457.0699 | 31730.1929
Total annual costs | [€/a] | 342523.5699 | 311739.2912
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 11
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: PANET
Agglomeration 2: HARTAU
Agglomeration 3: CUIESD
Agglomeration 4: BERGHIA
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2307 | 2307
Size of agglomeration 2 | [PE] | 296 | 296
Size of agglomeration 3 | [PE] | 789 | 789
Size of agglomeration 4 | [PE] | 239 | 239
Size of agglomeration 1+ 2+3+4 | [PE] |  | 3631
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 230.7
Wastewater amount of agglomeration 2 | [m³/d] | 29.6
Wastewater amount of agglomeration 3 | [m³/d] | 78.9
Wastewater amount of agglomeration 4 | [m³/d] | 23.9
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 363.1
Connection details
Lenth of the transportation line | [m] | - | 12500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 245700 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 44600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 93900
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 38900
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 378100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 2131250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 423100 | 2509350
Writting-off period | [years] | 40 | 40
| [€/a] | 10577.5 | 62733.75
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12693 | 75280.5
Annual costs civil works | [€/a] | 23270.5 | 138014.25
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 361050 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 59400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 133350
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 50850
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 559650
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 604650 | 559650
Writting-off period | [years] | 12 | 12
| [€/a] | 50387.5 | 46637.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 18139.5 | 16789.5
Annual costs mechanical and electrical equipment | [€/a] | 68527 | 63427
Annual costs I. (Investment) | [€/a] | 91797.5 | 201441.25
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 24186 | 22386
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 230.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 217.9983 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 29.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9584 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 57.9673 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 78.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6854 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 132.9782 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 23.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0235 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 48.3628 | -
Total A 1 | [kWh/d] | 457.3065
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 108.5
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 363.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3342
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 484.4312
Total A 1 - A 2 | [kWh/d] | 457.3065 | 484.4312
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 68.596 | 72.6647
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 68.596 | 72.6647
Annual costs IV. (consumption) | [€/a] | 25037.5332 | 26522.6068
Summary
Annual costs I. (Investment) | [€/a] | 91797.5 | 201441.25
Annual costs II. (Maintenance / Repairs) | [€/a] | 24186 | 22386
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 25037.5332 | 26522.6068
Total annual costs | [€/a] | 316221.0332 | 294149.8568
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 13
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1:SANGEORGIU DE PADURE
Agglomeration 2: VIFOROASA
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 5223 | 5223
Size of agglomeration 2 | [PE] | 877 | 877
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2+3+4 | [PE] |  | 6100
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 718.1625
Wastewater amount of agglomeration 2 | [m³/d] | 87.7
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 805.8625
Connection details
Lenth of the transportation line | [m] | - | 3000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 543.7433 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 509.6008
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 1135988.5897 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 102700
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 1243426.0454
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 511500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 1238688.5897 | 1754926.0454
Writting-off period | [years] | 40 | 40
| [€/a] | 30967.2147 | 43873.1511
Cost of capital, average | [%] | 3 | 3
| [€/a] | 37160.6577 | 52647.7814
Annual costs civil works | [€/a] | 68127.8724 | 96520.9325
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 1703982.8845 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 146550
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 1865139.0681
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 1850532.8845 | 1865139.0681
Writting-off period | [years] | 12 | 12
| [€/a] | 154211.0737 | 155428.2557
Cost of capital, average | [%] | 3 | 3
| [€/a] | 55515.9865 | 55954.172
Annual costs mechanical and electrical equipment | [€/a] | 209727.0602 | 211382.4277
Annual costs I. (Investment) | [€/a] | 277854.9327 | 307903.3602
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 74021.3154 | 74605.5627
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 718.1625 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 678.6226 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 87.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6583 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 145.4361 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 824.0587
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 87.7
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 805.8625
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2323
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 993.0539
Total A 1 - A 2 | [kWh/d] | 824.0587 | 993.0539
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 123.6088 | 148.9581
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 123.6088 | 148.9581
Annual costs IV. (consumption) | [€/a] | 45117.2147 | 54369.6986
Summary
Annual costs I. (Investment) | [€/a] | 277854.9327 | 307903.3602
Annual costs II. (Maintenance / Repairs) | [€/a] | 74021.3154 | 74605.5627
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 45117.2147 | 54369.6986
Total annual costs | [€/a] | 484593.4628 | 480678.6216
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 14
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: MIERCUREA NIRAJULUI
Agglomeration 2: DUMITRESTI
Agglomeration 3: SARDU NIRAJULUI+LAURENI+TAMPA (group)
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 6010 | 6010
Size of agglomeration 2 | [PE] | 338 | 338
Size of agglomeration 3 | [PE] | 1228 | 1228
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 7576
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 826.375
Wastewater amount of agglomeration 2 | [m³/d] | 33.8
Wastewater amount of agglomeration 3 | [m³/d] | 122.8
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 982.975
Connection details
Lenth of the transportation line | [m] | - | 7500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 512.7754 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3 (according formula) | [€/PE] | - | 465.4906
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 1232712.0682 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 48800
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 137800
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 1410622.7325
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 1278750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 1419312.0682 | 2725695.7325
Writting-off period | [years] | 40 | 40
| [€/a] | 35482.8017 | 68142.3933
Cost of capital, average | [%] | 3 | 3
| [€/a] | 42579.362 | 81770.872
Annual costs civil works | [€/a] | 78062.1638 | 149913.2653
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 1849068.1023 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 65700
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 199200
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 2115934.0988
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 2113968.1023 | 2119634.0988
Writting-off period | [years] | 12 | 12
| [€/a] | 176164.0085 | 176636.1749
Cost of capital, average | [%] | 3 | 3
| [€/a] | 63419.0431 | 63589.023
Annual costs mechanical and electrical equipment | [€/a] | 239583.0516 | 240225.1979
Annual costs I. (Investment) | [€/a] | 317645.2153 | 390138.4632
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 84558.7241 | 84785.364
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 826.375 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 780.8773 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 33.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.919 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 64.8613 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 122.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.575 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 193.414 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 1039.1525
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 156.6
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 7.1123
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 982.975
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.1921
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 1171.78
Total A 1 - A 2 | [kWh/d] | 1039.1525 | 1178.8922
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 155.8729 | 176.8338
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 155.8729 | 176.8338
Annual costs IV. (consumption) | [€/a] | 56893.6019 | 64544.3486
Summary
Annual costs I. (Investment) | [€/a] | 317645.2153 | 390138.4632
Annual costs II. (Maintenance / Repairs) | [€/a] | 84558.7241 | 84785.364
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 56893.6019 | 64544.3486
Total annual costs | [€/a] | 590497.5413 | 583268.1757
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 15
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: IBANESTI
Agglomeration 2: HODAC
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2559 | 2559
Size of agglomeration 2 | [PE] | 2273 | 2273
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2 | [PE] |  | 4832
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 255.9
Wastewater amount of agglomeration 2 | [m³/d] | 227.3
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 483.2
Connection details
Lenth of the transportation line | [m] | - | 1000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 270900 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 242300
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 498200
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 170500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 513200 | 705023
Writting-off period | [years] | 40 | 40
| [€/a] | 12830 | 17625.575
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15396 | 21150.69
Annual costs civil works | [€/a] | 28226 | 38776.265
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 398850 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 355950
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 739800
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 754800 | 743500
Writting-off period | [years] | 12 | 12
| [€/a] | 62900 | 61958.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 22644 | 22305
Annual costs mechanical and electrical equipment | [€/a] | 85544 | 84263.3333
Annual costs I. (Investment) | [€/a] | 113770 | 123039.5983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 30192 | 29740
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 255.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 241.8109 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 227.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.4333 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 325.7991 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 567.61
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 227.3
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 10.3232
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 483.2
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.277
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 617.0679
Total A 1 - A 2 | [kWh/d] | 567.61 | 627.3911
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 85.1415 | 94.1087
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 85.1415 | 94.1087
Annual costs IV. (consumption) | [€/a] | 31076.6495 | 34349.6625
Summary
Annual costs I. (Investment) | [€/a] | 113770 | 123039.5983
Annual costs II. (Maintenance / Repairs) | [€/a] | 30192 | 29740
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 31076.6495 | 34349.6625
Total annual costs | [€/a] | 262638.6495 | 230929.2609
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 16
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: FITCAU
Agglomeration 2: ALUNIS
Agglomeration 3: LUNCA MURESULUI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 489
Size of agglomeration 2 | [PE] | 2036 | 2036
Size of agglomeration 3 | [PE] | 775 | 775
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2+3+4 | [PE] |  | 2811
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 48.9
Wastewater amount of agglomeration 2 | [m³/d] | 203.6
Wastewater amount of agglomeration 3 | [m³/d] | 77.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 330
Connection details
Lenth of the transportation line | [m] | - | 7000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 63900 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 218600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 92500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 296100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1193500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 375000 | 1489600
Writting-off period | [years] | 40 | 40
| [€/a] | 9375 | 37240
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11250 | 44688
Annual costs civil works | [€/a] | 20625 | 81928
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 88350 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 320400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 131250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 436650
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 540000 | 436650
Writting-off period | [years] | 12 | 12
| [€/a] | 45000 | 36387.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 16200 | 13099.5
Annual costs mechanical and electrical equipment | [€/a] | 61200 | 49487
Annual costs I. (Investment) | [€/a] | 81825 | 131415
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 21600 | 17466
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 48.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 46.2077 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 203.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.4577 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 296.7903 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 77.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.69 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 130.9771 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 473.9752
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 281.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 330
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3875
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 457.8668
Total A 1 - A 2 | [kWh/d] | 473.9752 | 457.8668
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 71.0963 | 68.68
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 71.0963 | 68.68
Annual costs IV. (consumption) | [€/a] | 25950.1407 | 25068.2098
Summary
Annual costs I. (Investment) | [€/a] | 81825 | 131415
Annual costs II. (Maintenance / Repairs) | [€/a] | 21600 | 17466
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 25950.1407 | 25068.2098
Total annual costs | [€/a] | 304575.1407 | 217749.2098
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 18
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: CRACIUNESTI
Agglomeration 2: TRIMIOARA+CANTA (group)
Agglomeration 3: CORNESTI
Agglomeration 4: STEJERIS
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2700 | 2700
Size of agglomeration 2 | [PE] | 535 | 535
Size of agglomeration 3 | [PE] | 916 | 916
Size of agglomeration 4 | [PE] | 355 | 355
Size of agglomeration 1+ 2+3+4 | [PE] |  | 4506
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 270
Wastewater amount of agglomeration 2 | [m³/d] | 53.5
Wastewater amount of agglomeration 3 | [m³/d] | 91.6
Wastewater amount of agglomeration 4 | [m³/d] | 35.5
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 450.6
Connection details
Lenth of the transportation line | [m] | - | 5000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4 (according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 285000 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 68500
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 106600
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 50500
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 465600
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 852500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 510600 | 1354423
Writting-off period | [years] | 40 | 40
| [€/a] | 12765 | 33860.575
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15318 | 40632.69
Annual costs civil works | [€/a] | 28083 | 74493.265
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 420000 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 95250
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 152400
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 68250
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 690900
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 735900 | 694600
Writting-off period | [years] | 12 | 12
| [€/a] | 61325 | 57883.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 22077 | 20838
Annual costs mechanical and electrical equipment | [€/a] | 83402 | 78721.3333
Annual costs I. (Investment) | [€/a] | 111485 | 153214.5983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 29436 | 27784
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 270 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 255.1346 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 53.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7887 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 95.6949 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 91.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6473 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 150.8951 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 35.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9046 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 67.6136 | -
Total A 1 | [kWh/d] | 569.3382
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 145.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 6.59
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 450.6
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2908
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 581.6231
Total A 1 - A 2 | [kWh/d] | 569.3382 | 588.213
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 85.4007 | 88.232
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 85.4007 | 88.232
Annual costs IV. (consumption) | [€/a] | 31171.2668 | 32204.6622
Summary
Annual costs I. (Investment) | [€/a] | 111485 | 153214.5983
Annual costs II. (Maintenance / Repairs) | [€/a] | 29436 | 27784
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 31171.2668 | 32204.6622
Total annual costs | [€/a] | 347292.2668 | 257003.2606
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 19
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: EREMITU+MATRICI (group)
Agglomeration 2: CALUGARENI
Agglomeration 3: DAMIENI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2611 | 2611
Size of agglomeration 2 | [PE] | 612 | 612
Size of agglomeration 3 | [PE] | 273 | 273
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 3496
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 261.1
Wastewater amount of agglomeration 2 | [m³/d] | 61.2
Wastewater amount of agglomeration 3 | [m³/d] | 27.3
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 349.6
Connection details
Lenth of the transportation line | [m] | - | 7000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 276100 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 76200
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 42300
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 364600
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1193500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 394600 | 1558100
Writting-off period | [years] | 40 | 40
| [€/a] | 9865 | 38952.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11838 | 46743
Annual costs civil works | [€/a] | 21703 | 85695.5
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 406650 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 106800
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 55950
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 539400
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 569400 | 539400
Writting-off period | [years] | 12 | 12
| [€/a] | 47450 | 44950
Cost of capital, average | [%] | 3 | 3
| [€/a] | 17082 | 16182
Annual costs mechanical and electrical equipment | [€/a] | 64532 | 61132
Annual costs I. (Investment) | [€/a] | 86235 | 146827.5
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 22776 | 21576
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 261.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 246.7246 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 61.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7522 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 107.2372 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 27.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9828 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 54.1292 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 408.0911
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 88.5
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 349.6
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3419
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 469.1335
Total A 1 - A 2 | [kWh/d] | 408.0911 | 469.1335
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 61.2137 | 70.37
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 61.2137 | 70.37
Annual costs IV. (consumption) | [€/a] | 22342.988 | 25685.0618
Summary
Annual costs I. (Investment) | [€/a] | 86235 | 146827.5
Annual costs II. (Maintenance / Repairs) | [€/a] | 22776 | 21576
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 22342.988 | 25685.0618
Total annual costs | [€/a] | 262753.988 | 237888.5618
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 20
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: GLODENI
Agglomeration 2: PACURENI
Agglomeration 3: PAIGENI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2518 | 2518
Size of agglomeration 2 | [PE] | 265 | 265
Size of agglomeration 3 | [PE] | 458 | 458
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2+3 | [PE] |  | 3241
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 251.8
Wastewater amount of agglomeration 2 | [m³/d] | 26.5
Wastewater amount of agglomeration 3 | [m³/d] | 45.8
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 324.1
Connection details
Lenth of the transportation line | [m] | - | 7500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 266800 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 41500
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 60800
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 339100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1278750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 369100 | 1617850
Writting-off period | [years] | 40 | 40
| [€/a] | 9227.5 | 40446.25
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11073 | 48535.5
Annual costs civil works | [€/a] | 20300.5 | 88981.75
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 392700 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 54750
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 83700
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 501150
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 531150 | 501150
Writting-off period | [years] | 12 | 12
| [€/a] | 44262.5 | 41762.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15934.5 | 15034.5
Annual costs mechanical and electrical equipment | [€/a] | 60197 | 56797
Annual costs I. (Investment) | [€/a] | 80497.5 | 145778.75
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 21246 | 20046
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 251.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 237.9366 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 26.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9918 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 52.7828 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 45.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8318 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 83.8944 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 374.6139
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 72.3
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 324.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3576
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 439.9871
Total A 1 - A 2 | [kWh/d] | 374.6139 | 439.9871
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 56.1921 | 65.9981
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 56.1921 | 65.9981
Annual costs IV. (consumption) | [€/a] | 20510.1088 | 24089.2927
Summary
Annual costs I. (Investment) | [€/a] | 80497.5 | 145778.75
Annual costs II. (Maintenance / Repairs) | [€/a] | 21246 | 20046
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 20510.1088 | 24089.2927
Total annual costs | [€/a] | 253653.6088 | 233714.0427
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 21
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: ZAU DE CAMPIE+GAURA SANGERULUI (group)
Agglomeration 2: BOTEI
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2978 | 2978
Size of agglomeration 2 | [PE] | 157 | 157
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2 | [PE] |  | 3135
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 297.8
Wastewater amount of agglomeration 2 | [m³/d] | 15.7
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 313.5
Connection details
Lenth of the transportation line | [m] | - | 3000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 312800 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 30700
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 328500
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 511500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 343500 | 876323
Writting-off period | [years] | 40 | 40
| [€/a] | 8587.5 | 21908.075
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10305 | 26289.69
Annual costs civil works | [€/a] | 18892.5 | 48197.765
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 461700 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 38550
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 485250
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 500250 | 488950
Writting-off period | [years] | 12 | 12
| [€/a] | 41687.5 | 40745.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15007.5 | 14668.5
Annual costs mechanical and electrical equipment | [€/a] | 56695 | 55414.3333
Annual costs I. (Investment) | [€/a] | 75587.5 | 103612.0983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 20010 | 19558
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 297.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 281.404 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 15.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.158 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 33.8808 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 315.2848
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 15.7
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0.71304
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 313.5
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3645
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 427.7691
Total A 1 - A 2 | [kWh/d] | 315.2848 | 428.4822
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 47.2927 | 64.2723
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 47.2927 | 64.2723
Annual costs IV. (consumption) | [€/a] | 17261.8424 | 23459.3983
Summary
Annual costs I. (Investment) | [€/a] | 75587.5 | 103612.0983
Annual costs II. (Maintenance / Repairs) | [€/a] | 20010 | 19558
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 17261.8424 | 23459.3983
Total annual costs | [€/a] | 200459.3424 | 190429.4967
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 22
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: TAURENI+FANATE+MOARA DE JOS (group)
Agglomeration 2: VALEA LARGA+VALEA PADURII+PODURI+VALEA SURII+VALEA FRATIEI+VALEA GLODULUI+VALEA URIESULUI+GRADINI
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1049 | 1049
Size of agglomeration 2 | [PE] | 3374 | 3374
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2 | [PE] |  | 4423
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 104.9
Wastewater amount of agglomeration 2 | [m³/d] | 337.4
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 442.3
Connection details
Lenth of the transportation line | [m] | - | 4500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 119900 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 352400
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 457300
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 767250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 472300 | 1260873
Writting-off period | [years] | 40 | 40
| [€/a] | 11807.5 | 31521.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 14169 | 37826.19
Annual costs civil works | [€/a] | 25976.5 | 69348.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 172350 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 521100
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 678450
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 693450 | 682150
Writting-off period | [years] | 12 | 12
| [€/a] | 57787.5 | 56845.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 20803.5 | 20464.5
Annual costs mechanical and electrical equipment | [€/a] | 78591 | 77310.3333
Annual costs I. (Investment) | [€/a] | 104567.5 | 146658.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 27738 | 27286
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 104.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 99.1245 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 337.4 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.3492 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 455.2311 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 554.3556
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 337.4
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 15.3236
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 442.3
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2945
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 572.537
Total A 1 - A 2 | [kWh/d] | 554.3556 | 587.8605
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 83.1533 | 88.1791
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 83.1533 | 88.1791
Annual costs IV. (consumption) | [€/a] | 30350.9699 | 32185.3648
Summary
Annual costs I. (Investment) | [€/a] | 104567.5 | 146658.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 27738 | 27286
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 30350.9699 | 32185.3648
Total annual costs | [€/a] | 250256.4699 | 249929.7132
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 24
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: GHEORGHE DOJA+ILIENI+SATU NOU+ TRIMIA (group)
Agglomeration 2: LEORDENI
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2486 | 2486
Size of agglomeration 2 | [PE] | 383 | 383
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+ 2 | [PE] |  | 2869
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 248.6
Wastewater amount of agglomeration 2 | [m³/d] | 38.3
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 286.9
Connection details
Lenth of the transportation line | [m] | - | 2000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 263600 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 53300
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 301900
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 341000
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 316900 | 679223
Writting-off period | [years] | 40 | 40
| [€/a] | 7922.5 | 16980.575
Cost of capital, average | [%] | 3 | 3
| [€/a] | 9507 | 20376.69
Annual costs civil works | [€/a] | 17429.5 | 37357.265
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 387900 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 72450
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 445350
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 460350 | 449050
Writting-off period | [years] | 12 | 12
| [€/a] | 38362.5 | 37420.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 13810.5 | 13471.5
Annual costs mechanical and electrical equipment | [€/a] | 52173 | 50892.3333
Annual costs I. (Investment) | [€/a] | 69602.5 | 88249.5983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 18414 | 17962
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 248.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 234.9128 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 38.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8826 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 72.1036 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 307.0164
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 38.3
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 1.7395
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 286.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3831
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 396.8239
Total A 1 - A 2 | [kWh/d] | 307.0164 | 398.5634
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 46.0525 | 59.7845
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 46.0525 | 59.7845
Annual costs IV. (consumption) | [€/a] | 16809.1489 | 21821.3455
Summary
Annual costs I. (Investment) | [€/a] | 69602.5 | 88249.5983
Annual costs II. (Maintenance / Repairs) | [€/a] | 18414 | 17962
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 16809.1489 | 21821.3455
Total annual costs | [€/a] | 192425.6489 | 171832.9439
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 25
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: VANATORI
Agglomeration 2: SOARD
Agglomeration 3: MURENI
Agglomeration 4: FELEAG
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1793 | 1793
Size of agglomeration 2 | [PE] | 649 | 649
Size of agglomeration 3 | [PE] | 367 | 367
Size of agglomeration 4 | [PE] | 222 | 222
Size of agglomeration 1+2+3+4 | [PE] |  | 3031
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 179.3
Wastewater amount of agglomeration 2 | [m³/d] | 64.9
Wastewater amount of agglomeration 3 | [m³/d] | 36.7
Wastewater amount of agglomeration 4 | [m³/d] | 22.2
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 303.1
Connection details
Lenth of the transportation line | [m] | - | 12500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 194300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 79900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 51700
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 37200
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 318100
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 2131250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 363100 | 2485673
Writting-off period | [years] | 40 | 40
| [€/a] | 9077.5 | 62141.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10893 | 74570.19
Annual costs civil works | [€/a] | 19970.5 | 136712.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 283950 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 112350
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 70050
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 48300
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 469650
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 514650 | 473350
Writting-off period | [years] | 12 | 12
| [€/a] | 42887.5 | 39445.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15439.5 | 14200.5
Annual costs mechanical and electrical equipment | [€/a] | 58327 | 53646.3333
Annual costs I. (Investment) | [€/a] | 78297.5 | 190358.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 20586 | 18934
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 179.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 169.4283 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 64.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7366 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 112.7031 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 36.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8949 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 69.5443 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 22.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0465 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 45.4331 | -
Total A 1 | [kWh/d] | 397.1088
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 101.6
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 4.6143
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 303.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3716
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 415.7201
Total A 1 - A 2 | [kWh/d] | 397.1088 | 420.3344
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 59.5663 | 63.0502
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 59.5663 | 63.0502
Annual costs IV. (consumption) | [€/a] | 21741.7049 | 23013.3081
Summary
Annual costs I. (Investment) | [€/a] | 78297.5 | 190358.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 20586 | 18934
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 21741.7049 | 23013.3081
Total annual costs | [€/a] | 295825.2049 | 276105.6564
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 26
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SASCHIZ
Agglomeration 2: CLOARSTEF
Agglomeration 3: MIHAI VITEAZU
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1563 | 1563
Size of agglomeration 2 | [PE] | 197 | 197
Size of agglomeration 3 | [PE] | 319 | 319
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2+3 | [PE] |  | 2079
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 156.3
Wastewater amount of agglomeration 2 | [m³/d] | 19.7
Wastewater amount of agglomeration 3 | [m³/d] | 31.9
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 207.9
Connection details
Lenth of the transportation line | [m] | - | 9000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 171300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 34700
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 46900
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 222900
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1534500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 252900 | 1757400
Writting-off period | [years] | 40 | 40
| [€/a] | 6322.5 | 43935
Cost of capital, average | [%] | 3 | 3
| [€/a] | 7587 | 52722
Annual costs civil works | [€/a] | 13909.5 | 96657
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 249450 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 44550
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 62850
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 326850
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 356850 | 326850
Writting-off period | [years] | 12 | 12
| [€/a] | 29737.5 | 27237.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10705.5 | 9805.5
Annual costs mechanical and electrical equipment | [€/a] | 40443 | 37043
Annual costs I. (Investment) | [€/a] | 54352.5 | 133700
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 14274 | 13074
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 156.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 147.6946 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 19.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0843 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 41.061 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 31.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.936 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 61.7598 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 250.5154
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 51.6
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 207.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4531
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 302.0903
Total A 1 - A 2 | [kWh/d] | 250.5154 | 302.0903
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 37.5773 | 45.3135
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 37.5773 | 45.3135
Annual costs IV. (consumption) | [€/a] | 13715.7188 | 16539.4454
Summary
Annual costs I. (Investment) | [€/a] | 54352.5 | 133700
Annual costs II. (Maintenance / Repairs) | [€/a] | 14274 | 13074
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 13715.7188 | 16539.4454
Total annual costs | [€/a] | 213742.2188 | 207113.4454
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 27
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: NADES
Agglomeration 2: TIGMANDRU
Agglomeration 3: MAGHERUS
Agglomeration 4: PIPEA
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1228 | 1228
Size of agglomeration 2 | [PE] | 931 | 931
Size of agglomeration 3 | [PE] | 148 | 148
Size of agglomeration 4 | [PE] | 99 | 99
Size of agglomeration 1+2+3+4 | [PE] |  | 2406
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 122.8
Wastewater amount of agglomeration 2 | [m³/d] | 93.1
Wastewater amount of agglomeration 3 | [m³/d] | 14.8
Wastewater amount of agglomeration 4 | [m³/d] | 9.9
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 240.6
Connection details
Lenth of the transportation line | [m] | - | 13000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 137800 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 108100
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 29800
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 24900
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 255600
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 2216500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 300600 | 2472100
Writting-off period | [years] | 40 | 40
| [€/a] | 7515 | 61802.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 9018 | 74163
Annual costs civil works | [€/a] | 16533 | 135965.5
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 199200 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 154650
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 37200
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 29850
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 375900
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 420900 | 375900
Writting-off period | [years] | 12 | 12
| [€/a] | 35075 | 31325
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12627 | 11277
Annual costs mechanical and electrical equipment | [€/a] | 47702 | 42602
Annual costs I. (Investment) | [€/a] | 64235 | 178567.5
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 16836 | 15036
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 122.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 116.039 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 93.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6432 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 152.9852 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 14.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.1776 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 32.2285 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 9.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.3159 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 22.9271 | -
Total A 1 | [kWh/d] | 324.1798
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 107.9
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 240.6
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4209
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 341.8732
Total A 1 - A 2 | [kWh/d] | 324.1798 | 341.8732
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 48.627 | 51.281
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 48.627 | 51.281
Annual costs IV. (consumption) | [€/a] | 17748.8446 | 18717.5602
Summary
Annual costs I. (Investment) | [€/a] | 64235 | 178567.5
Annual costs II. (Maintenance / Repairs) | [€/a] | 16836 | 15036
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 17748.8446 | 18717.5602
Total annual costs | [€/a] | 274019.8446 | 256121.0602
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 28
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BALAUSERI+AGRISTEU
Agglomeration 2: CHENDU+DUMITRENI
Agglomeration 3: SENEREUS
Agglomeration 4: FILITELNIC
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2013 | 2013
Size of agglomeration 2 | [PE] | 2056 | 2056
Size of agglomeration 3 | [PE] | 725 | 725
Size of agglomeration 4 | [PE] | 200 | 200
Size of agglomeration 1+2+3+4 | [PE] |  | 4994
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 201.3
Wastewater amount of agglomeration 2 | [m³/d] | 205.6
Wastewater amount of agglomeration 3 | [m³/d] | 72.5
Wastewater amount of agglomeration 4 | [m³/d] | 20
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 499.4
Connection details
Lenth of the transportation line | [m] | - | 14700 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 216300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 220600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 87500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 35000
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 514400
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 2506350
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 559400 | 3057073
Writting-off period | [years] | 40 | 40
| [€/a] | 13985 | 76426.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 16782 | 91712.19
Annual costs civil works | [€/a] | 30767 | 168139.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 316950 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 323400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 123750
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 45000
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 764100
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 809100 | 767800
Writting-off period | [years] | 12 | 12
| [€/a] | 67425 | 63983.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 24273 | 23034
Annual costs mechanical and electrical equipment | [€/a] | 91698 | 87017.3333
Annual costs I. (Investment) | [€/a] | 122465 | 255156.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 32364 | 30712
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 201.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 190.217 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 205.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.4555 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 299.2576 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 72.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7074 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 123.7845 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 20 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0795 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 41.5899 | -
Total A 1 | [kWh/d] | 654.849
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 278.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 12.6304
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 499.4
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2706
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 634.5443
Total A 1 - A 2 | [kWh/d] | 654.849 | 647.1746
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 98.2273 | 97.0762
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 98.2273 | 97.0762
Annual costs IV. (consumption) | [€/a] | 35852.9807 | 35432.8113
Summary
Annual costs I. (Investment) | [€/a] | 122465 | 255156.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 32364 | 30712
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 35852.9807 | 35432.8113
Total annual costs | [€/a] | 365881.9807 | 365101.1596
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 29
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SUPLAC
Agglomeration 2: IDRIFAIA
Agglomeration 3: LASLAU MARE
Agglomeration 4: LASLAU MIC
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2420 | 2420
Size of agglomeration 2 | [PE] | 693 | 693
Size of agglomeration 3 | [PE] | 436 | 436
Size of agglomeration 4 | [PE] | 406 | 406
Size of agglomeration 1+2+3+4 | [PE] |  | 3955
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 242
Wastewater amount of agglomeration 2 | [m³/d] | 69.3
Wastewater amount of agglomeration 3 | [m³/d] | 43.6
Wastewater amount of agglomeration 4 | [m³/d] | 40.6
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 395.5
Connection details
Lenth of the transportation line | [m] | - | 10500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 257000 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 84300
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 58600
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 55600
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 410500
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 1790250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 455500 | 2237073
Writting-off period | [years] | 40 | 40
| [€/a] | 11387.5 | 55926.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 13665 | 67112.19
Annual costs civil works | [€/a] | 25052.5 | 123039.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 378000 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 118950
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 80400
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 75900
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 608250
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 653250 | 611950
Writting-off period | [years] | 12 | 12
| [€/a] | 54437.5 | 50995.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 19597.5 | 18358.5
Annual costs mechanical and electrical equipment | [€/a] | 74035 | 69354.3333
Annual costs I. (Investment) | [€/a] | 99087.5 | 192393.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 26130 | 24478
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 242 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 228.6762 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 69.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7192 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 119.1414 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 43.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8456 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 80.4687 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 40.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8659 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 75.7542 | -
Total A 1 | [kWh/d] | 504.0405
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 112.9
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 5.1275
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 395.5
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3168
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 520.7979
Total A 1 - A 2 | [kWh/d] | 504.0405 | 525.9254
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 75.6061 | 78.8888
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 75.6061 | 78.8888
Annual costs IV. (consumption) | [€/a] | 27596.2177 | 28794.4172
Summary
Annual costs I. (Investment) | [€/a] | 99087.5 | 192393.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 26130 | 24478
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 27596.2177 | 28794.4172
Total annual costs | [€/a] | 328013.7177 | 289465.7656
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 30
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BAHNEA+BERNADEA
Agglomeration 2: LEPINDEA
Agglomeration 3: DAIA
Agglomeration 4: IDICIU
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2141 | 2141
Size of agglomeration 2 | [PE] | 204 | 204
Size of agglomeration 3 | [PE] | 227 | 227
Size of agglomeration 4 | [PE] | 347 | 347
Size of agglomeration 1+2+3+4 | [PE] |  | 2919
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 214.1
Wastewater amount of agglomeration 2 | [m³/d] | 20.4
Wastewater amount of agglomeration 3 | [m³/d] | 22.7
Wastewater amount of agglomeration 4 | [m³/d] | 34.7
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 291.9
Connection details
Lenth of the transportation line | [m] | - | 9000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 229100 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 35400
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 37700
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 49700
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 306900
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1534500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 351900 | 1841400
Writting-off period | [years] | 40 | 40
| [€/a] | 8797.5 | 46035
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10557 | 55242
Annual costs civil works | [€/a] | 19354.5 | 101277
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 336150 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 45600
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 49050
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 67050
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 452850
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 497850 | 452850
Writting-off period | [years] | 12 | 12
| [€/a] | 41487.5 | 37737.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 14935.5 | 13585.5
Annual costs mechanical and electrical equipment | [€/a] | 56423 | 51323
Annual costs I. (Investment) | [€/a] | 75777.5 | 152600
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 19914 | 18114
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 214.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 202.3123 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 20.4 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0732 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 42.2933 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 22.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0396 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 46.2982 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 34.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9113 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 66.321 | -
Total A 1 | [kWh/d] | 357.2248
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 43.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 291.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3795
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 402.6731
Total A 1 - A 2 | [kWh/d] | 357.2248 | 402.6731
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 53.5837 | 60.401
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 53.5837 | 60.401
Annual costs IV. (consumption) | [€/a] | 19558.0566 | 22046.3517
Summary
Annual costs I. (Investment) | [€/a] | 75777.5 | 152600
Annual costs II. (Maintenance / Repairs) | [€/a] | 19914 | 18114
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 19558.0566 | 22046.3517
Total annual costs | [€/a] | 290449.5566 | 236560.3517
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 31
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: MICA+CEAUS (group)
Agglomeration 2: DEAJ+HARANGLAB (group)
Agglomeration 3: ABUS
Agglomeration 4: PAUCISOARA
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1652 | 1652
Size of agglomeration 2 | [PE] | 2380 | 2380
Size of agglomeration 3 | [PE] | 363 | 363
Size of agglomeration 4 | [PE] | 235 | 235
Size of agglomeration 1+2+3+4 | [PE] |  | 4630
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 165.2
Wastewater amount of agglomeration 2 | [m³/d] | 238
Wastewater amount of agglomeration 3 | [m³/d] | 36.3
Wastewater amount of agglomeration 4 | [m³/d] | 23.5
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 463
Connection details
Lenth of the transportation line | [m] | - | 14500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 180200 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 253000
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 51300
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 38500
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 478000
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 2472250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 523000 | 2986573
Writting-off period | [years] | 40 | 40
| [€/a] | 13075 | 74664.325
Cost of capital, average | [%] | 3 | 3
| [€/a] | 15690 | 89597.19
Annual costs civil works | [€/a] | 28765 | 164261.515
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 262800 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 372000
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 69450
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 50250
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 709500
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 754500 | 713200
Writting-off period | [years] | 12 | 12
| [€/a] | 62875 | 59433.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 22635 | 21396
Annual costs mechanical and electrical equipment | [€/a] | 85510 | 80829.3333
Annual costs I. (Investment) | [€/a] | 114275 | 245090.8483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 30180 | 28528
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 165.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 156.1046 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 238 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.4233 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 338.7419 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 36.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8981 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 68.9018 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 23.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0288 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 47.6764 | -
Total A 1 | [kWh/d] | 611.4247
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 274.3
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 12.4578
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 463
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.2854
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 595.1499
Total A 1 - A 2 | [kWh/d] | 611.4247 | 607.6077
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 91.7137 | 91.1412
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 91.7137 | 91.1412
Annual costs IV. (consumption) | [€/a] | 33475.5 | 33266.5233
Summary
Annual costs I. (Investment) | [€/a] | 114275 | 245090.8483
Annual costs II. (Maintenance / Repairs) | [€/a] | 30180 | 28528
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 33475.5 | 33266.5233
Total annual costs | [€/a] | 353130.5 | 350685.3717
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 32
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: OGRA
Agglomeration 2: DILEU VECHI
Agglomeration 3: VAIDEIU
Agglomeration 4: GIULUS
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1556 | 1556
Size of agglomeration 2 | [PE] | 239 | 239
Size of agglomeration 3 | [PE] | 172 | 172
Size of agglomeration 4 | [PE] | 209 | 209
Size of agglomeration 1+2+3+4 | [PE] |  | 2176
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 155.6
Wastewater amount of agglomeration 2 | [m³/d] | 23.9
Wastewater amount of agglomeration 3 | [m³/d] | 17.2
Wastewater amount of agglomeration 4 | [m³/d] | 20.9
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 217.6
Connection details
Lenth of the transportation line | [m] | - | 12000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 170600 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 38900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 32200
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 35900
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 232600
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 2046000
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 277600 | 2314923
Writting-off period | [years] | 40 | 40
| [€/a] | 6940 | 57873.075
Cost of capital, average | [%] | 3 | 3
| [€/a] | 8328 | 69447.69
Annual costs civil works | [€/a] | 15268 | 127320.765
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 248400 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 50850
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 40800
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 46350
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 341400
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 386400 | 345100
Writting-off period | [years] | 12 | 12
| [€/a] | 32200 | 28758.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11592 | 10353
Annual costs mechanical and electrical equipment | [€/a] | 43792 | 39111.3333
Annual costs I. (Investment) | [€/a] | 59060 | 166432.0983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 15456 | 13804
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 155.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 147.0331 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 23.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0235 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 48.3628 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 17.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.1281 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 36.6028 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 20.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0655 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 43.1696 | -
Total A 1 | [kWh/d] | 275.1683
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 41.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 1.8666
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 217.6
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4429
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 313.9852
Total A 1 - A 2 | [kWh/d] | 275.1683 | 315.8518
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 41.2752 | 47.3778
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 41.2752 | 47.3778
Annual costs IV. (consumption) | [€/a] | 15065.4647 | 17292.887
Summary
Annual costs I. (Investment) | [€/a] | 59060 | 166432.0983
Annual costs II. (Maintenance / Repairs) | [€/a] | 15456 | 13804
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 15065.4647 | 17292.887
Total annual costs | [€/a] | 264781.4647 | 241328.9854
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 34
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: VARGATA+VALEA+MITRESTI (group)
Agglomeration 2: GRAUSORUL
Agglomeration 3: VADU
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1493 | 1493
Size of agglomeration 2 | [PE] | 216 | 216
Size of agglomeration 3 | [PE] | 295 | 295
Size of agglomeration 4 | [PE] | 0 | 0
Size of agglomeration 1+2+3 | [PE] |  | 2004
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 149.3
Wastewater amount of agglomeration 2 | [m³/d] | 21.6
Wastewater amount of agglomeration 3 | [m³/d] | 29.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 200.4
Connection details
Lenth of the transportation line | [m] | - | 8000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 164300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 36600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 44500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 215400
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1364000
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 245400 | 1579400
Writting-off period | [years] | 40 | 40
| [€/a] | 6135 | 39485
Cost of capital, average | [%] | 3 | 3
| [€/a] | 7362 | 47382
Annual costs civil works | [€/a] | 13497 | 86867
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 238950 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 47400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 59250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 315600
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 345600 | 315600
Writting-off period | [years] | 12 | 12
| [€/a] | 28800 | 26300
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10368 | 9468
Annual costs mechanical and electrical equipment | [€/a] | 39168 | 35768
Annual costs I. (Investment) | [€/a] | 52665 | 122635
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 13824 | 12624
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 149.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 141.08 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 21.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0551 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 44.391 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 29.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9594 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 57.8014 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 243.2723
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 51.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 200.4
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4613
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 292.835
Total A 1 - A 2 | [kWh/d] | 243.2723 | 292.835
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 36.4909 | 43.9253
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 36.4909 | 43.9253
Annual costs IV. (consumption) | [€/a] | 13319.1604 | 16032.718
Summary
Annual costs I. (Investment) | [€/a] | 52665 | 122635
Annual costs II. (Maintenance / Repairs) | [€/a] | 13824 | 12624
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 13319.1604 | 16032.718
Total annual costs | [€/a] | 211208.1604 | 195091.718
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 35
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1:BLIDIREASA+ZIMTI+BRADUTELU+PARAU MARE+DULCEA+IBANESTI PADURE (group)
Agglomeration 2: TIREU
Agglomeration 3: TISIEU
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1493 | 1493
Size of agglomeration 2 | [PE] | 216 | 216
Size of agglomeration 3 | [PE] | 295 | 295
Size of agglomeration 4 | [PE] | 0 | 0
Size of agglomeration 1+2+3 | [PE] |  | 2004
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 149.3
Wastewater amount of agglomeration 2 | [m³/d] | 21.6
Wastewater amount of agglomeration 3 | [m³/d] | 29.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 200.4
Connection details
Lenth of the transportation line | [m] | - | 2000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 164300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 36600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 44500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 215400
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 341000
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 245400 | 556400
Writting-off period | [years] | 40 | 40
| [€/a] | 6135 | 13910
Cost of capital, average | [%] | 3 | 3
| [€/a] | 7362 | 16692
Annual costs civil works | [€/a] | 13497 | 30602
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 238950 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 47400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 59250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 315600
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 345600 | 315600
Writting-off period | [years] | 12 | 12
| [€/a] | 28800 | 26300
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10368 | 9468
Annual costs mechanical and electrical equipment | [€/a] | 39168 | 35768
Annual costs I. (Investment) | [€/a] | 52665 | 66370
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 13824 | 12624
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 149.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 141.08 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 21.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.0551 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 44.391 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 29.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9594 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 57.8014 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 243.2723
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 51.1
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 200.4
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4613
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 292.835
Total A 1 - A 2 | [kWh/d] | 243.2723 | 292.835
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 36.4909 | 43.9253
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 36.4909 | 43.9253
Annual costs IV. (consumption) | [€/a] | 13319.1604 | 16032.718
Summary
Annual costs I. (Investment) | [€/a] | 52665 | 66370
Annual costs II. (Maintenance / Repairs) | [€/a] | 13824 | 12624
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 13319.1604 | 16032.718
Total annual costs | [€/a] | 211208.1604 | 138826.718
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 36
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: DUBISTEA DE PADURE
Agglomeration 2: BUCASU
Agglomeration 3: TOACA
Agglomeration 4: URICEA
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 439 | 439
Size of agglomeration 2 | [PE] | 140 | 140
Size of agglomeration 3 | [PE] | 1673 | 1673
Size of agglomeration 4 | [PE] | 57 | 57
Size of agglomeration 1+2+3+4 | [PE] |  | 2309
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 43.9
Wastewater amount of agglomeration 2 | [m³/d] | 14
Wastewater amount of agglomeration 3 | [m³/d] | 167.3
Wastewater amount of agglomeration 4 | [m³/d] | 5.7
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 230.9
Connection details
Lenth of the transportation line | [m] | - | 4500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 58900 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 29000
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 182300
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 20700
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 245900
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 767250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 290900 | 1013150
Writting-off period | [years] | 40 | 40
| [€/a] | 7272.5 | 25328.75
Cost of capital, average | [%] | 3 | 3
| [€/a] | 8727 | 30394.5
Annual costs civil works | [€/a] | 15999.5 | 55723.25
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 80850 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 36000
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 265950
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 23550
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 361350
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 406350 | 361350
Writting-off period | [years] | 12 | 12
| [€/a] | 33862.5 | 30112.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12190.5 | 10840.5
Annual costs mechanical and electrical equipment | [€/a] | 46053 | 40953
Annual costs I. (Investment) | [€/a] | 62052.5 | 96676.25
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 16254 | 14454
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 43.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 41.483 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 14 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.1962 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 30.7469 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 167.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5022 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 251.3186 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 5.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.5201 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 14.3647 | -
Total A 1 | [kWh/d] | 337.9132
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 181.3
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 230.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4299
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 330.1639
Total A 1 - A 2 | [kWh/d] | 337.9132 | 330.1639
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 50.687 | 49.5246
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 50.687 | 49.5246
Annual costs IV. (consumption) | [€/a] | 18500.7463 | 18076.4734
Summary
Annual costs I. (Investment) | [€/a] | 62052.5 | 96676.25
Annual costs II. (Maintenance / Repairs) | [€/a] | 16254 | 14454
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 18500.7463 | 18076.4734
Total annual costs | [€/a] | 272007.2463 | 173006.7234
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 37
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1:GLAJARIE+LARGA (group)
Agglomeration 2: FUNDOAIA
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1925 | 1925
Size of agglomeration 2 | [PE] | 138 | 138
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2 | [PE] |  | 2063
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 192.5
Wastewater amount of agglomeration 2 | [m³/d] | 13.8
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 206.3
Connection details
Lenth of the transportation line | [m] | - | 3000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 207500 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 28800
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 221300
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 511500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 236300 | 732800
Writting-off period | [years] | 40 | 40
| [€/a] | 5907.5 | 18320
Cost of capital, average | [%] | 3 | 3
| [€/a] | 7089 | 21984
Annual costs civil works | [€/a] | 12996.5 | 40304
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 303750 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 35700
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 324450
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 339450 | 324450
Writting-off period | [years] | 12 | 12
| [€/a] | 28287.5 | 27037.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 10183.5 | 9733.5
Annual costs mechanical and electrical equipment | [€/a] | 38471 | 36771
Annual costs I. (Investment) | [€/a] | 51467.5 | 77075
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 13578 | 12978
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 192.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 181.9015 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 13.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.2011 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 30.3745 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 212.276
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 13.8
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 206.3
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4548
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 300.1202
Total A 1 - A 2 | [kWh/d] | 212.276 | 300.1202
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 31.8414 | 45.018
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 31.8414 | 45.018
Annual costs IV. (consumption) | [€/a] | 11622.1136 | 16431.5818
Summary
Annual costs I. (Investment) | [€/a] | 51467.5 | 77075
Annual costs II. (Maintenance / Repairs) | [€/a] | 13578 | 12978
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 11622.1136 | 16431.5818
Total annual costs | [€/a] | 164267.6136 | 150284.5818
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 38
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: RASTOLITA+ANDRENEASCA (group)
Agglomeration 2: GALAOAIA
Agglomeration 3: BORZIA
Agglomeration 4: IOD
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1437 | 1437
Size of agglomeration 2 | [PE] | 326 | 326
Size of agglomeration 3 | [PE] | 91 | 91
Size of agglomeration 4 | [PE] | 376 | 376
Size of agglomeration 1+2+3+4 | [PE] |  | 2230
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 143.7
Wastewater amount of agglomeration 2 | [m³/d] | 32.6
Wastewater amount of agglomeration 3 | [m³/d] | 9.1
Wastewater amount of agglomeration 4 | [m³/d] | 37.6
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 223
Connection details
Lenth of the transportation line | [m] | - | 9500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 158700 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 47600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 24100
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 52600
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 238000
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 1619750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 283000 | 1894073
Writting-off period | [years] | 40 | 40
| [€/a] | 7075 | 47351.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 8490 | 56822.19
Annual costs civil works | [€/a] | 15565 | 104174.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 230550 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 63900
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 28650
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 71400
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 349500
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 394500 | 353200
Writting-off period | [years] | 12 | 12
| [€/a] | 32875 | 29433.3333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11835 | 10596
Annual costs mechanical and electrical equipment | [€/a] | 44710 | 40029.3333
Annual costs I. (Investment) | [€/a] | 60275 | 144203.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 15780 | 14128
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 143.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 135.7883 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 32.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.9296 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 62.9057 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 9.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.3459 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 21.348 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 37.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8879 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 70.986 | -
Total A 1 | [kWh/d] | 291.028
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 41.7
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 1.8939
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 223
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4375
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 320.5717
Total A 1 - A 2 | [kWh/d] | 291.028 | 322.4656
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 43.6542 | 48.3698
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 43.6542 | 48.3698
Annual costs IV. (consumption) | [€/a] | 15933.782 | 17654.9927
Summary
Annual costs I. (Investment) | [€/a] | 60275 | 144203.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 15780 | 14128
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 15933.782 | 17654.9927
Total annual costs | [€/a] | 267188.782 | 219786.341
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 39
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SUSENI
Agglomeration 2: LUIERIU
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1554 | 1554
Size of agglomeration 2 | [PE] | 765 | 765
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2 | [PE] |  | 2319
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 155.4
Wastewater amount of agglomeration 2 | [m³/d] | 76.5
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 231.9
Connection details
Lenth of the transportation line | [m] | - | 4500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 170400 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 91500
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 246900
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 767250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 261900 | 1014150
Writting-off period | [years] | 40 | 40
| [€/a] | 6547.5 | 25353.75
Cost of capital, average | [%] | 3 | 3
| [€/a] | 7857 | 30424.5
Annual costs civil works | [€/a] | 14404.5 | 55778.25
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 248100 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 129750
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 362850
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 377850 | 362850
Writting-off period | [years] | 12 | 12
| [€/a] | 31487.5 | 30237.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11335.5 | 10885.5
Annual costs mechanical and electrical equipment | [€/a] | 42823 | 41123
Annual costs I. (Investment) | [€/a] | 57227.5 | 96901.25
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 15114 | 14514
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 155.4 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 146.8441 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 76.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6934 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 129.5444 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 276.3886
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 76.5
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 231.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.429
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 331.3745
Total A 1 - A 2 | [kWh/d] | 276.3886 | 331.3745
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 41.4583 | 49.7062
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 41.4583 | 49.7062
Annual costs IV. (consumption) | [€/a] | 15132.2739 | 18142.7527
Summary
Annual costs I. (Investment) | [€/a] | 57227.5 | 96901.25
Annual costs II. (Maintenance / Repairs) | [€/a] | 15114 | 14514
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 15132.2739 | 18142.7527
Total annual costs | [€/a] | 175073.7739 | 173358.0027
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 40
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BATOS
Agglomeration 2: GORENI
Agglomeration 3: DEDRAD
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1355 | 1355
Size of agglomeration 2 | [PE] | 690 | 690
Size of agglomeration 3 | [PE] | 1526 | 1526
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2+3 | [PE] |  | 3571
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 135.5
Wastewater amount of agglomeration 2 | [m³/d] | 69
Wastewater amount of agglomeration 3 | [m³/d] | 152.6
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 357.1
Connection details
Lenth of the transportation line | [m] | - | 10000 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 150500 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 84000
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 167600
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 372100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1705000
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 402100 | 2077100
Writting-off period | [years] | 40 | 40
| [€/a] | 10052.5 | 51927.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12063 | 62313
Annual costs civil works | [€/a] | 22115.5 | 114240.5
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 218250 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 118500
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 243900
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 550650
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 580650 | 550650
Writting-off period | [years] | 12 | 12
| [€/a] | 48387.5 | 45887.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 17419.5 | 16519.5
Annual costs mechanical and electrical equipment | [€/a] | 65807 | 62407
Annual costs I. (Investment) | [€/a] | 87922.5 | 176647.5
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 23226 | 22026
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 135.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 128.0398 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 69 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7204 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 118.7045 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 152.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5235 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 232.4867 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 479.231
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 221.6
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 357.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3376
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 477.6432
Total A 1 - A 2 | [kWh/d] | 479.231 | 477.6432
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 71.8847 | 71.6465
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 71.8847 | 71.6465
Annual costs IV. (consumption) | [€/a] | 26237.8976 | 26150.9639
Summary
Annual costs I. (Investment) | [€/a] | 87922.5 | 176647.5
Annual costs II. (Maintenance / Repairs) | [€/a] | 23226 | 22026
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 26237.8976 | 26150.9639
Total annual costs | [€/a] | 268786.3976 | 268624.4639
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 41
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BREAZA
Agglomeration 2: FILPISU MARE
Agglomeration 3: FILPISU MIC
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1207 | 1207
Size of agglomeration 2 | [PE] | 869 | 869
Size of agglomeration 3 | [PE] | 455 | 455
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2+3 | [PE] |  | 2531
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 120.7
Wastewater amount of agglomeration 2 | [m³/d] | 86.9
Wastewater amount of agglomeration 3 | [m³/d] | 45.5
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 253.1
Connection details
Lenth of the transportation line | [m] | - | 9500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 135700 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 101900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 60500
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 268100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1619750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 298100 | 1887850
Writting-off period | [years] | 40 | 40
| [€/a] | 7452.5 | 47196.25
Cost of capital, average | [%] | 3 | 3
| [€/a] | 8943 | 56635.5
Annual costs civil works | [€/a] | 16395.5 | 103831.75
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 196050 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 145350
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 83250
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 394650
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 424650 | 394650
Writting-off period | [years] | 12 | 12
| [€/a] | 35387.5 | 32887.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12739.5 | 11839.5
Annual costs mechanical and electrical equipment | [€/a] | 48127 | 44727
Annual costs I. (Investment) | [€/a] | 64522.5 | 148558.75
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 16986 | 15786
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 120.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 114.0546 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 86.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6607 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 144.3118 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 45.5 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8336 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 83.4287 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 341.7951
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 132.4
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 253.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4099
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 356.8568
Total A 1 - A 2 | [kWh/d] | 341.7951 | 356.8568
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 51.2693 | 53.5285
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 51.2693 | 53.5285
Annual costs IV. (consumption) | [€/a] | 18713.2826 | 19537.9095
Summary
Annual costs I. (Investment) | [€/a] | 64522.5 | 148558.75
Annual costs II. (Maintenance / Repairs) | [€/a] | 16986 | 15786
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 18713.2826 | 19537.9095
Total annual costs | [€/a] | 231621.7826 | 227682.6595
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 42
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: CEAUSU DE CAMPIE+CAMPENITA+HERGHELIA (group)
Agglomeration 2: PORUMBENI
Agglomeration 3: VOINICENI
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 2590 | 2590
Size of agglomeration 2 | [PE] | 556 | 556
Size of agglomeration 3 | [PE] | 946 | 946
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2+3 | [PE] |  | 4092
No. of WTP modules | [items] | 3
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 259
Wastewater amount of agglomeration 2 | [m³/d] | 55.6
Wastewater amount of agglomeration 3 | [m³/d] | 94.6
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2+3 | [m³/d] |  | 409.2
Connection details
Lenth of the transportation line | [m] | - | 9500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2+3(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 274000 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 70600
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 109600
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 424200
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 1619750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 454200 | 2043950
Writting-off period | [years] | 40 | 40
| [€/a] | 11355 | 51098.75
Cost of capital, average | [%] | 3 | 3
| [€/a] | 13626 | 61318.5
Annual costs civil works | [€/a] | 24981 | 112417.25
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 403500 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 98400
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 156900
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 628800
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 658800 | 628800
Writting-off period | [years] | 12 | 12
| [€/a] | 54900 | 52400
Cost of capital, average | [%] | 3 | 3
| [€/a] | 19764 | 18864
Annual costs mechanical and electrical equipment | [€/a] | 74664 | 71264
Annual costs I. (Investment) | [€/a] | 99645 | 183681.25
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 26352 | 25152
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 26280 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 131400 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 259 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 244.7402 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 55.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7782 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 98.8666 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 94.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.6392 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 155.0701 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 498.677
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 150.2
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 409.2
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.31
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 536.0362
Total A 1 - A 2 | [kWh/d] | 498.677 | 536.0362
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 74.8015 | 80.4054
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 74.8015 | 80.4054
Annual costs IV. (consumption) | [€/a] | 27302.5631 | 29347.9829
Summary
Annual costs I. (Investment) | [€/a] | 99645 | 183681.25
Annual costs II. (Maintenance / Repairs) | [€/a] | 26352 | 25152
Annual costs III. (labour) | [€/a] | 131400 | 43800
Annual costs IV. (consumption) | [€/a] | 27302.5631 | 29347.9829
Total annual costs | [€/a] | 284699.5631 | 281981.2329
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 43
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SINCAI+LECHINCIOARA (group)
Agglomeration 2: CULPIU
Agglomeration 3: SABED
Agglomeration 4: BOZED
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1207 | 1207
Size of agglomeration 2 | [PE] | 402 | 402
Size of agglomeration 3 | [PE] | 743 | 743
Size of agglomeration 4 | [PE] | 182 | 182
Size of agglomeration 1+2+3+4 | [PE] |  | 2534
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 120.7
Wastewater amount of agglomeration 2 | [m³/d] | 40.2
Wastewater amount of agglomeration 3 | [m³/d] | 74.3
Wastewater amount of agglomeration 4 | [m³/d] | 18.2
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 253.4
Connection details
Lenth of the transportation line | [m] | - | 14500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 135700 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 55200
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 89300
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 33200
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 268400
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 2472250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 313400 | 2740650
Writting-off period | [years] | 40 | 40
| [€/a] | 7835 | 68516.25
Cost of capital, average | [%] | 3 | 3
| [€/a] | 9402 | 82219.5
Annual costs civil works | [€/a] | 17237 | 150735.75
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 196050 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 75300
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 126450
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 42300
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 395100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 440100 | 395100
Writting-off period | [years] | 12 | 12
| [€/a] | 36675 | 32925
Cost of capital, average | [%] | 3 | 3
| [€/a] | 13203 | 11853
Annual costs mechanical and electrical equipment | [€/a] | 49878 | 44778
Annual costs I. (Investment) | [€/a] | 67115 | 195513.75
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 17604 | 15804
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 120.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 114.0546 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 40.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8687 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 75.1216 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 74.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.701 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 126.3823 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 18.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.1097 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 38.3973 | -
Total A 1 | [kWh/d] | 353.9558
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 114.5
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 253.4
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4097
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 357.215
Total A 1 - A 2 | [kWh/d] | 353.9558 | 357.215
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 53.0934 | 53.5822
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 53.0934 | 53.5822
Annual costs IV. (consumption) | [€/a] | 19379.0803 | 19557.5205
Summary
Annual costs I. (Investment) | [€/a] | 67115 | 195513.75
Annual costs II. (Maintenance / Repairs) | [€/a] | 17604 | 15804
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 19379.0803 | 19557.5205
Total annual costs | [€/a] | 279298.0803 | 274675.2705
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 45
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SANPETRU DE CAMPIE+BARLIBASA (group)
Agglomeration 2: DAMBU+SATU NOU (group)
Agglomeration 3: TUSINU
Agglomeration 4: SANGEORGIU DE CAMPIE
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1253 | 1253
Size of agglomeration 2 | [PE] | 851 | 851
Size of agglomeration 3 | [PE] | 649 | 649
Size of agglomeration 4 | [PE] | 428 | 428
Size of agglomeration 1+2+3+4 | [PE] |  | 3181
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 125.3
Wastewater amount of agglomeration 2 | [m³/d] | 85.1
Wastewater amount of agglomeration 3 | [m³/d] | 64.9
Wastewater amount of agglomeration 4 | [m³/d] | 42.8
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 318.1
Connection details
Lenth of the transportation line | [m] | - | 13500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | G
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 140300 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 100100
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 79900
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 57800
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 333100
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) Transportation line | [€] | - | 2301750
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 378100 | 2634850
Writting-off period | [years] | 40 | 40
| [€/a] | 9452.5 | 65871.25
Cost of capital, average | [%] | 3 | 3
| [€/a] | 11343 | 79045.5
Annual costs civil works | [€/a] | 20795.5 | 144916.75
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 202950 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 142650
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 112350
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 79200
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 492150
(3) Pumping station agglomeration 1 (if necessary) | [€] | -
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 537150 | 492150
Writting-off period | [years] | 12 | 12
| [€/a] | 44762.5 | 41012.5
Cost of capital, average | [%] | 3 | 3
| [€/a] | 16114.5 | 14764.5
Annual costs mechanical and electrical equipment | [€/a] | 60877 | 55777
Annual costs I. (Investment) | [€/a] | 81672.5 | 200693.75
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 21486 | 19686
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 125.3 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 118.4014 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 85.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.666 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 141.7762 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 64.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7366 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 112.7031 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 42.8 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.8509 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 79.2165 | -
Total A 1 | [kWh/d] | 452.0971
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 150
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 0
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 0
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 318.1
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3615
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 433.0789
Total A 1 - A 2 | [kWh/d] | 452.0971 | 433.0789
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 67.8146 | 64.9618
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 67.8146 | 64.9618
Annual costs IV. (consumption) | [€/a] | 24752.3166 | 23711.0697
Summary
Annual costs I. (Investment) | [€/a] | 81672.5 | 200693.75
Annual costs II. (Maintenance / Repairs) | [€/a] | 21486 | 19686
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 24752.3166 | 23711.0697
Total annual costs | [€/a] | 303110.8166 | 287890.8197
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 49
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: SAES
Agglomeration 2: VULCAN
Agglomeration 3: DAIA
Agglomeration 4: APOLD
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1196 | 1196
Size of agglomeration 2 | [PE] | 109 | 109
Size of agglomeration 3 | [PE] | 557 | 557
Size of agglomeration 4 | [PE] | 861 | 861
Size of agglomeration 1+2+3+4 | [PE] |  | 2723
No. of WTP modules | [items] | 4
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 119.6
Wastewater amount of agglomeration 2 | [m³/d] | 10.9
Wastewater amount of agglomeration 3 | [m³/d] | 55.7
Wastewater amount of agglomeration 4 | [m³/d] | 86.1
Wastewater amount of agglomeration 1+ 2+3+4 | [m³/d] |  | 272.3
Connection details
Lenth of the transportation line | [m] | - | 14500 | centralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 1+2+3+4(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 134600 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 25900
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 70700
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 101100
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 287300
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 2472250
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 332300 | 2795873
Writting-off period | [years] | 40 | 40
| [€/a] | 8307.5 | 69896.825
Cost of capital, average | [%] | 3 | 3
| [€/a] | 9969 | 83876.19
Annual costs civil works | [€/a] | 18276.5 | 153773.015
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 194400 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 31350
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 98550
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 144150
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 423450
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 468450 | 427150
Writting-off period | [years] | 12 | 12
| [€/a] | 39037.5 | 35595.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 14053.5 | 12814.5
Annual costs mechanical and electrical equipment | [€/a] | 53091 | 48410.3333
Annual costs I. (Investment) | [€/a] | 71367.5 | 202183.3483
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 18738 | 17086
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 35040 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 175200 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 119.6 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 113.0152 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 10.9 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 2.282 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 24.8738 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 55.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.7777 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 99.0172 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 86.1 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.663 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 143.1858 | -
Total A 1 | [kWh/d] | 380.092
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 66.6
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 3.0248
A 2.2 WWTP agglomeration 1+2+3+4
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 272.3
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.3942
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 379.6538
Total A 1 - A 2 | [kWh/d] | 380.092 | 382.6785
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 57.0138 | 57.4018
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 57.0138 | 57.4018
Annual costs IV. (consumption) | [€/a] | 20810.0377 | 20951.6482
Summary
Annual costs I. (Investment) | [€/a] | 71367.5 | 202183.3483
Annual costs II. (Maintenance / Repairs) | [€/a] | 18738 | 17086
Annual costs III. (labour) | [€/a] | 175200 | 43800
Annual costs IV. (consumption) | [€/a] | 20810.0377 | 20951.6482
Total annual costs | [€/a] | 286115.5377 | 284020.9965
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP

## Agglomeration 51
Master Plan, Chapter 5, Option Analysis on Wastewater Agglomerations
County: Mures
Agglomeration 1: BAGACIU
Agglomeration 2: DELENI
Agglomeration 3:
Agglomeration 4:
|  | Option 1 | Option 2
Data Base
Size of agglomeration 1 | [PE] | 1342 | 1342
Size of agglomeration 2 | [PE] | 1247 | 1247
Size of agglomeration 3 | [PE] |  | 0
Size of agglomeration 4 | [PE] |  | 0
Size of agglomeration 1+2 | [PE] |  | 2589
No. of WTP modules | [items] | 2
Specific wastewater amount | [l/cap x d] | 80 | 80
Specific wastewater amount | [l/cap x d] | 110 | 110
Infiltration rate | [%] | 25 | 25
Wastewater amount of agglomeration 1 | [m³/d] | 134.2
Wastewater amount of agglomeration 2 | [m³/d] | 124.7
Wastewater amount of agglomeration 3 | [m³/d] | 0
Wastewater amount of agglomeration 4 | [m³/d] | 0
Wastewater amount of agglomeration 1+ 2 | [m³/d] |  | 258.9
Connection details
Lenth of the transportation line | [m] | - | 5000 | descentralized
Kind of connection (g = by gravity, p = by pressure main) | [-] | - | P
Diameter of the transportation line | [mm] | - | 250
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Costs
Specfic price WWTP agglomeration 1 (according formula) | [€/PE] | 250 | -
Specfic price WWTP agglomeration 2 (according formula) | [€/PE] | 250
Specfic price WWTP agglomeration 3 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 4 (according formula) | [€/PE] | 0
Specfic price WWTP agglomeration 1+2(according formula) | [€/PE] | - | 250
Specific price transportation line (according Unit Price Data Base) | [€/m] | - | 170.5
I. Investment costs
A. Civil works
(1.1) WWTP for agglomeration 1 (40 % of total costs) | [€] | 149200 | -
(1.2) WWTP for agglomeration 2 (40 % of total costs) | [€] | 139700
(1.3) WWTP for agglomeration 3 (40 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (40 % of total costs) | [€] | 0
(2) WWTP for agglomeration (40 % of total costs) | [€] |  | 273900
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 36323
(4) Transportation line | [€] | - | 852500
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs civil works | [€] | 288900 | 1162723
Writting-off period | [years] | 40 | 40
| [€/a] | 7222.5 | 29068.075
Cost of capital, average | [%] | 3 | 3
| [€/a] | 8667 | 34881.69
Annual costs civil works | [€/a] | 15889.5 | 63949.765
B. Mechanical and electrical equipment
(1.1) WWTP for agglomeration 1 (60 % of total costs) | [€] | 216300 | -
(1.2) WWTP for agglomeration 2 (60 % of total costs) | [€] | 202050
(1.3) WWTP for agglomeration 3 (60 % of total costs) | [€] | 0
(1.4) WWTP for agglomeration 4 (60 % of total costs) | [€] | 0
(2) WWTP for agglomeration (60% of total costs) | [€] | - | 403350
(3) Pumping station agglomeration 1 (if necessary) | [€] | - | 3700
(4) free | [€]
(5) free | [€]
(6) free | [€]
(7) free | [€]
(8) free | [€]
(9) free | [€]
(10) free | [€]
Total costs mechanical and electricial equipment | [€] | 418350 | 407050
Writting-off period | [years] | 12 | 12
| [€/a] | 34862.5 | 33920.8333
Cost of capital, average | [%] | 3 | 3
| [€/a] | 12550.5 | 12211.5
Annual costs mechanical and electrical equipment | [€/a] | 47413 | 46132.3333
Annual costs I. (Investment) | [€/a] | 63302.5 | 110082.0983
II. Maintenance / Repairs
in % of the mechanical and electrical equipment installed | [%/a] | 4 | 4
Annual costs II. (Maintenance / Repairs) | [€/a] | 16734 | 16282
III. Labour costs
specific labour costs | [€/h] | 5 | 5
annual expenses option 1 (2 full-time workers/module) | [h/a] | 17520 | -
annual expenses option 2 (2 full-time workers) | [h/a] | - | 8760
Annual costs III. (labour) | [€/a] | 87600 | 43800
IV. Operation costs consumption
A. Energy consumption
A 1 - Option 1
A 1.1 WWTP agglomeration 1
Wastewater amount of agglomeration 1 | [m³/d] | 134.2 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0.94494 | -
Daily energy consumption WWTP agglomeration 1 | [kWh/d] | 126.8113 | -
A 1.2 WWTP agglomeration 2
Wastewater amount of agglomeration 2 | [m³/d] | 124.7 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 1.5713 | -
Daily energy consumption WWTP agglomeration 2 | [kWh/d] | 195.9454 | -
A 1.3 WWTP agglomeration 3
Wastewater amount of agglomeration 3 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 3 | [kWh/d] | 0 | -
A 1.4 WWTP agglomeration 4
Wastewater amount of agglomeration 4 | [m³/d] | 0 | -
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] | 0 | -
Daily energy consumption WWTP agglomeration 4 | [kWh/d] | 0 | -
Total A 1 | [kWh/d] | 322.7568
A 2 - Option 2
A 2.1 Pumping station agglomeration 1 (if necessary)
Wastewater amount of agglomeration 1 | [m³/d] | - | 124.7
Maximum difference in height Dh (only in case of pumping station) | [m] | - | 10
Daily energy consumption pumping station agglomeration 1 | [kWh/d] | - | 5.6635
A 2.2 WWTP agglomeration 1+2
Specfic price WWTP agglomeration 2 (according formula) | [m³/d] |  | 258.9
Specific energy consumption WWTP agglomeration 1 (acc. formula) | [kWh/m³] |  | 1.4051
Daily energy consumption WWTP agglomeration 2 | [kWh/d] |  | 363.7704
Total A 1 - A 2 | [kWh/d] | 322.7568 | 369.4339
Specific energy price | [netto €/kWh] | 0.15 | 0.15
Energy costs | [€/d] | 48.4135 | 55.4151
B. Chemicals consumption
The difference in the consumption of chemicals is neglectable.
C. Sludge disposal
The sludge amounts produced in both options is almost the same.
The difference in the sludge disposal costs is neglectable.
Total IV. | [€/d] | 48.4135 | 55.4151
Annual costs IV. (consumption) | [€/a] | 17670.934 | 20226.5051
Summary
Annual costs I. (Investment) | [€/a] | 63302.5 | 110082.0983
Annual costs II. (Maintenance / Repairs) | [€/a] | 16734 | 16282
Annual costs III. (labour) | [€/a] | 87600 | 43800
Annual costs IV. (consumption) | [€/a] | 17670.934 | 20226.5051
Total annual costs | [€/a] | 185307.434 | 190390.6034
Conclusion : according to the option analysis the Consultant proposed centralized solution to be followed.
Option 1 - decentral wastewater treatment of agglomeration 1
Option 2 - central wastewater treatment
Agglomeration2
Agglomeration2
WWTP
WWTP
WWTP